##### GENERAL

Furnish and install ENVIRO-TEC® Model CDV Vertical Concealed Direct Drive Fan Coil Unit where indicated on the plans and specifications.  Units shall be completely factory assembled, tested and shipped as one piece except where noted.

All units shall be capable of meeting or exceeding the scheduled capacities for cooling, heating, and air delivery.  All unit dimensions for each model and size shall be considered maximums.  Units shall be ETL listed in compliance with UL/ANSI Standard 1995, and be certified as complying with the latest edition of ARI Standard 440.

##### CONSTRUCTION

All units shall be fabricated of heavy gauge galvanized steel, able to meet 125 hour salt spray test per ASTM B-117.  Casing shall be internally lined with 1/2" thick fiberglass insulation, rated for a maximum air velocity of 5000 f.p.m.  Maximum thermal conductivity shall be .24 (BTU • in) / (hr • ft2 • °F). Insulation must meet all requirements of ASTM C1071 (including C665), UL 181 for erosion, and carry a 25/50 rating for flame spread/smoke developed per ASTM E-84, UL 723 and NFPA 90A.

All units shall have a minimum 1" duct collar on the discharge.  All access panels shall be fully insulated and attached with standard fasteners on at least two opposite sides.  No coil, drain piping, or electrical connections shall pass through any access panel.

Option: Provide foil faced insulation in lieu of matt faced insulation.  Foil insulation shall meet or exceed the requirements stated above, and in addition meet ASTM Standards C-665 and C-1136 for mold, mildew, and humidity resistance. Insulation shall be lined with aluminum foil, fiberglass scrim reinforcement, and #30 kraft paper laminated together with a flame resistant adhesive.  All exposed edges shall be sealed to prevent any fibers from reaching the air stream.

Each unit shall be furnished with a one-piece heavy gauge G90 steel drain pan with welded corner construction.

Option: Provide a single wall primary drain pan constructed entirely of heavy gauge type 304 stainless steel for superior corrosion resistance.  Stainless steel drain pans shall meet or exceed the requirements stated above.

##### SOUND

Units shall have published sound power level data tested in accordance with ARI Standard 350-86.

##### FAN ASSEMBLY

Unit fan shall be dynamically balanced, forwardly curved, direct drive DWDI wheel with 18 gauge galvanized chromate coated double inlet scroll.  Motor shall include torsion flex suspension mount affixed to scroll using

permanently attached mounting studs.  Motor mount shall be secured with Nylock® lock nuts.  Blower scroll shall be mounted to fan bulkhead with 18 gauge mounting rail in a manner to allow no metal-to-metal contact with fan bulkhead.

Blower motor shall be high efficiency, permanently lubricated sleeve bearing, permanent split-capacitor type with thermal overload protection and three separate horsepower taps.  Single speed motors are not acceptable.  The fan motor shall be unpluggable from the electrical leads at the motor case for simplified removal.

Option: Provide an electronic (SCR) fan speed controller for aid in balancing the fan capacity.  The speed controller shall have a turn down stop to prevent the possibility of harming the motor bearings, and incorporate electrical noise suppression to minimize noise on the incoming power lines.

##### COILS

All unit coils shall be rated in accordance with ARI 410.

All coils shall be 1/2" O.D. seamless copper tubes with collared and corrugated aluminum fins.  All tubes shall be mechanically expanded to provide an efficient bond between tube and fin.  All water coils shall be provided with a manual air vent fitting to allow for coil venting.  Valve core type vent fittings shall not be accepted.

All chilled water, hot water, and direct expansion (DX) coils shall have 0.0055" thick aluminum fins and 0.016" tube wall thickness.

All coils shall be hydrostatically tested with air under water at 450 PSIG minimum pressure and rated for a maximum of 300 PSIG working pressure at 200°F.

DX coils shall be tested to 450 PSIG pressure and factory sealed and charged with a minimum of 5 PSIG nitrogen or refrigerated dry air.  DX coils shall be provided with a fixed orifice metering device (distributor-eliminator).

##### OPTIONS

Coil casing shall be fabricated from 304 Stainless Steel.

Provide automatic air vents, in lieu of manual air vents.

Fin material shall be (0.0075" thick aluminum) (0.0075" thick copper).

Tube wall thickness shall be 0.025" on chilled water, hot water, and direct expansion coils.

##### FILTER

All units shall be furnished with a minimum 1" nominal throwaway filter.  Provide optional 2" filter rack with 2" throwaway filter where indicated.  Filters shall be tight fitting to prevent air bypass.

##### DISCHARGE PLENUM SECTION

Provide a fully insulated integral discharge plenum section, complete with double deflection supply grille.  Discharge plenum sections shipped loose for field installation to the units are not acceptable.

##### MIXING BOX SECTION

Provide a fully insulated integral mixing box section, complete with return and outside air dampers.  Mixing box sections shipped loose for field installation to the units are not acceptable.

##### ELECTRICAL

Units shall be furnished with a single point power location and electrical junction box for motor and other electrical terminations.

ELECTRIC HEAT SECTION

Provide an integral electric resistance heating assembly with the heating capacity, voltage, kilowatts, and stages as shown in the schedule.

The heater assembly shall be designed and rated for installation to the air handling unit without the use of duct extensions or transitions between the unit and the heater assembly.  The heater shall be factory assembled and completely wired for single point power connection.

The heater and unit assembly shall be listed for zero clearance and shall meet all NEC

requirements, and be ETL listed with the unit as an assembly in compliance with UL/ANSI Standard 1995.

All heating elements shall be open coil design using Ni-Chrome wire mounted in ceramic insulators and housed in an insulated heavy gauge galvanized steel housing.  All elements shall terminate in a machine staked stainless steel terminal secured with stainless steel hardware for corrosion resistance.  The element support brackets shall be spaced no greater than 3-1/2" on center.  All internal wiring shall be rated for 105°C minimum.

All heaters shall include overtemperature protection, and shall be interlocked with the fan.  All heater elements shall be single stage unless noted otherwise on the plans.

An incoming line power distribution block shall be provided.  The power distribution block shall be designed to accept incoming power wiring capable of carrying 125% of the calculated load current.